Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice, Fifth Edition.

This section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” after editing this section.

Section numbers are from MasterFormat 2010 Update.

SECTION 26 05 33.22

EXPLOSION PROOF CONDUIT OUTLET BOXES

Specifier Notes:  Delete any information below in Parts 1, 2 or 3 which is not required or relevant for the project.

PART 1 – GENERAL

1.01	SUMMARY

A.	This section includes industrial grade conduit outlet boxes for use in hazardous locations where explosion-proof and dust ignition-proof construction is required.

B.	Related Sections:

1. 	Section 26 05 33.56 	Explosion Proof Conduit Outlet Bodies and Fittings

1.02	REFERENCES

A.	Underwriters Laboratories, Inc. (UL):

1.	UL886			Outlet Boxes and Fittings for Use in Hazardous (Classified)

Locations

B.	National Fire Protection Association (NFPA):

1.  	NFPA 70	 	National Electrical Code (NEC)

C.	Federal Specification

1.	A-A-50563		Conduit Outlet Boxes, Bodies, and Entrance Caps, Electrical

D.	Canadian Standard Association (CSA):

1. 	CSA C22.2 No. 30	Explosion-Proof Enclosures for Use in Class I Hazardous Locations

2.	CSA C22.1		Canadian Electrical Code Part I

E.	National Electrical Manufacturers Association (NEMA):

1.	NEMA 250		Enclosures for Electrical Equipment (1000 Volts Maximum)

1.03	SUBMITTALS

A.	Comply with Section 01 33 00 – Submittal Procedures.

B.	Product Data:

1. 	Submit manufacturer’s descriptive literature and product specifications for each product.

2. 	Manufacturer’s product drawings.

1.04	QUALITY ASSURANCE

A.	Manufacturer Qualifications: Products shall be free of defects in material and workmanship.

B.	Furnished products are listed or classified by third party agencies as suitable for the intended purpose.

  - WARRANTY

- Product is warranted free of defects in material and workmanship.

- Product is warranted to perform the intended function within design limits.

PART 2 – PRODUCTS

  - GENERAL

A.	Product covered in this section shall be suitable for explosion-proof and dust ignition-proof hazardous location areas as defined in the NEC and CEC.

B.	The following products shall be used in explosion-proof and dust ignition-proof hazardous locations.

1.	GU Series Ductile Iron Outlet Boxes

2.	GA Series Aluminum Outlet Boxes

3.	EXUN Series Aluminum Outlet Boxes with Internal Hubs

4.	GASS series Aluminum Square Outlet Boxes

5.	GUP Series Ductile Iron Square Outlet Boxes

C.	UL Listed product shall be listed to UL 886.

D.	CSA Certified product shall be certified to C22.2 No. 30.

E.	Conduit outlet boxes shall comply with Federal Specification A-A-50563.

2.02	MANUFACTURERS

A.	Acceptable Manufacturers:

Thomas & Betts Corporation

8155 T&B Blvd

Memphis, TN 38125

800-816-7809, 901-252-5000

www.tnb.com

Products:

- T&B® Outlet Boxes – Explosion-Proof, Dust Ignition-Proof

2.03	DESIGN AND PERFORMANCE REQUIREMENTS

- GU Series Ductile Iron Outlet Boxes

  - GU series outlet boxes shall be used for mounting of fixture outlets, allow for ease of wiring, provide a junction in conduit for wiring, to change direction in rigid conduit systems, and attach two or more pieces of conduit.

  - GU series outlet boxes shall be made from ductile iron with a zinc-plated and aluminum acrylic paint finish.

  - GU series outlet boxes shall use a die cast aluminum cover with an o-ring gasket.

  - GU series outlet boxes shall cover conduit hub trade sizes from 1/2' TO 2” with NPT tapered threads.

  - GU series outlet boxes shall come in ten different configurations: GUA, GUAB, GUAC, GUAD, GUAL, GUAM, GUAN, GUAT, GUAW AND GUAX.  Reference manufacturer’s literature for full details.

  - GU series outlet boxes shall have a minimum of five full threads and an internal bushing.

  - GU series outlet boxes shall be suitable for raintight and wet locations when used with the gasketed cover.

  - GU series outlet boxes shall have an internal ground boss and screw.

  - GU series outlet boxes shall be suitable for NEMA Types 3, 4, 7 CD and 9 EFG applications.

  - GU series outlet boxes shall be suitable for Class I, Division 1 & 2, Groups C, D; Class II, Division 1, Groups E,F,G; and Class III, Division 1 & 2.

  - GU series outlet boxes shall be UL Listed and CSA Certified.

- GA Series Aluminum Outlet Boxes

  - GA series outlet boxes shall be used as a junction for branch conduits; an accessible wiring chamber to pull wires; a means to make changes and splices; a support for installation of OEM devices.

  - GA series outlet boxes shall be made from die cast copper-free aluminum with an aluminum lacquer finish.

  - GA series outlet boxes shall have external hubs with NPT taper threads and an internal bushing for conduit trade sizes from 1/2" to 2”.

  - GA series outlet boxes shall come in seven configurations: GAC, GAE, GAL, GALB, GAT, GAX and GAJU.

  - GA series outlet boxes shall have three cover configurations: surface style GAS, dome style GAD, canopy style GAJ.

  - GA series outlet boxes shall have an internal ground boss and screws.

  - GA series outlet boxes shall be available with an o-ring (-OR suffix on catalog number) and be suitable for a NEMA Type 4 environment, raintight and wet location applications.

  - GA series outlet boxes shall be suitable for Class I, Division 1 & 2, Groups C, D; Class II, Division 1, Groups E,F,G; and Class III, Division 1 & 2.

  - GA series outlet boxes shall be UL Listed and CSA Certified.

- EXUN Series Aluminum Outlet Boxes with Internal Hubs

  - EXUN series outlet boxes shall be used as a junction for branch conduits; an accessible wiring chamber for maintenance, pulling of wires or making splices; for installations with limited space.

  - EXUN series outlet boxes shall be made from die cast copper-free aluminum with an aluminum lacquer finish.

  - EXUN series outlet boxes shall be available in 5-hole internal hub configuration (EXUN-1 series) and a 4-hole internal hub configuration (EXUN-11 series).

  - EXUN series outlet boxes shall have internal NPT threaded hubs for use in location with limited space.

  - EXUN series outlet boxes shall have conduit hub trade sizes from 1/2" to 1”.

  - EXUN series outlet boxes shall have an internal ground boss and screw.

  - EXUN series outlet boxes shall be suitable for a NEMA Types 3, 4, 7 CD and 9 EFG environments, raintight and wet location applications.

  - EXUN series outlet boxes shall be suitable for Class I, Division 1 & 2, Groups C, D; Class II, Division 1, Groups E,F,G; and Class III, Division 1 & 2.

  - EXUN series outlet boxes shall be UL Listed and CSA Certified.

- GASS series Aluminum Square Outlet Boxes

  - GASS series outlet boxes shall be used as a junction for branch conduits and an accessible wiring chamber for maintenance, changes, pulling wire and splicing.

  - GASS series outlet boxes shall be square shaped with extra wide 3-3/4” opening for more hand space.

  - GASS series outlet boxes shall be made from sand cast copper-free aluminum with an aluminum lacquer finish.

  - GASS series outlet box covers shall be made from die cast copper-free aluminum with an aluminum lacquer finish.

  - GASS series outlet boxes shall have NPT threaded hubs spaced for use with EXFU and EXMU 3-piece couplings (unions).

  - GASS series outlet boxes shall cover a conduit hub trade size from 1/2" to 1”.

  - GASS series outlet boxes shall have an internal ground boss and screw.

  - GASS series outlet boxes shall be suitable for a NEMA Types 3, 4, 7 CD and 9 EFG environments, raintight and wet location applications.

  - GASS series outlet boxes shall be suitable for Class I, Division 1 & 2, Groups C, D; Class II, Division 1, Groups E,F,G; and Class III, Division 1 & 2.

  - GASS series outlet boxes shall be UL Listed and CSA Certified.

- GUP Series Ductile Iron Square Outlet Boxes

  - GUP series outlet boxes shall have a compact design for use as a junction in environments where space is limited.

  - GUP series outlet boxes shall be made from ductile iron with electro-galvanized and aluminum acrylic paint finish.

  - GUP series outlet box covers shall be made from copper-free aluminum.

  - GUP series outlet boxes shall have a neoprene o-ring gasket.

  - GUP series outlet boxes shall be available with 10 3/4" NPT hubs (GUP214-TB) and 6 3/4" NPT hubs (GUP215-TB).

  - GUP series outlet boxes shall have an internal ground boss and screw.

  - GUP series outlet boxes shall be suitable for a NEMA Types 3, 4, 7 CD and 9 EFG environments, raintight and wet location applications.

  - GUP series outlet boxes shall be suitable for Class I, Division 1 & 2, Groups C, D; Class II, Division 1, Groups E,F,G; and Class III, Division 1 & 2.

  - GUP series outlet boxes shall be UL Listed and CSA Certified.

PART 3 – EXECUTION

3.01	INSTALLATION

- Installation shall be in accordance with the NEC and CEC guidelines where applicable, and

manufacturer’s instructions.

END OF SECTION