Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice, Fifth Edition.

This section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” after editing this section.

Section numbers are from MasterFormat 2010 Update.

SECTION 26 53 00

EXIT SIGNS

Specifier Notes:  Delete any information below in Parts 1, 2 or 3 which is not required or relevant for the project.

PART 1 – GENERAL

1.01	SUMMARY

A.	This section includes exit signs units with battery back-ups or remote fixture mounting for ordinary location use.

B.	Related Sections:

1. 	Section 26 54 00.01	Classified Location Exit Signs

1.02	REFERENCES

A.	Underwriters Laboratories, Inc. (UL):

1. 	UL924			Standard for Safety of Emergency Lighting and Power Equipment

B.	National Fire Prevention Association (NFPA):

1.	NFPA 101		Life Safety Code

C.	National Fire Protection Association (NFPA):

1.  	NFPA 70	 	National Electrical Code (NEC)

D.	Canadian Standards Association (CAS):

1.  	CSA C22.2 No.141	Unit Equipment for Emergency Lighting

2.	CSA C860		Performance of Internally Lighted Exit signs

3.	CSA C22.1		Canadian Electrical Code Part I (CEC)

1.03	SUBMITTALS

A.	Comply with Section 01 33 00 – Submittal Procedures.

B.	Product Data:

1. Submit manufacturer’s descriptive literature and product specifications for each product.

2. Manufacturer’s product drawings.

C.	Manufacturer’s installation instructions

1.04	QUALITY ASSURANCE

A.	Manufacturer Qualifications: Products shall be free of defects in material and workmanship.

- Furnished products are listed and/or certified by third party agencies as suitable for the intended purpose.

C.	All units will be certified that they have been tested prior to shipping.

  - WARRANTY

- Product is warranted free of defects in material and workmanship.

- Product is warranted to perform the intended function within design limits.

PART 2 – PRODUCTS

2.01	GENERAL

A.	Exit signs units shall be UL Listed and/or CSA Certified to

1) UL 924 for USA.

2) C22.2 No 141 and C860 for Canada

B.	Exit signs units shall perform self-testing in accordance with NFPA 101 if provided. This shall not be regulated in Canada.

2.02	MANUFACTURERS

A.	Acceptable Manufacturers:

Thomas & Betts Corporation

8155 T&B Blvd

Memphis, TN 38125

800-816-7809, 901-252-5000

www.tnb.com

Product:	EMERGI-LITE® Exit Sign Units

2.03	DESIGN AND PERFORMANCE REQUIREMENTS

- EXPK Series (AC only, AC/DC and self-powered):

    - The unit shall be NEMA 4X rated, with weather and corrosion-resistant.

    - The unit shall have a uniformly illuminated polycarbonate face, sealed push-to-test switch and special baffled venting system.

    - The unit shall be available in single or double face.

    - The LED light panel uses only 2 Watts of energy, has a 20 year expected lamp life, and superior, red, even illumination.

    - AC exit signs shall be either 120V or 277V.

    - AC/DC exit signs shall be either 120VAC or 277VAC, and 6, 12 or 24VDC.

    - Self-powered exit signs shall be 120/277V.

    - AC input for the normally-on circuit shall be 120/277V, 60 Hz, 0.025/0.12A, 30 W.

    - AC input for LED shall be 120/277V, 60 Hz, 2 W.

    - Battery output shall be 6 V fused circuit.

    - The unit charger shall be current limited, temperature compensated, short-circuit protected and reverse polarity protected.

    - The unit shall be available with the following sealed maintenance-free battery:

    - a.	Nickel-Cadmium

    - A Low voltage battery disconnect circuit automatically shuts down lamp load and circuitry when battery reaches 871/2% of its nominal voltage.

    - The unit shall be furnished with an electronic lockout circuit which will connect the battery when the AC circuit is activated, and an electronic brownout circuit which will activate the unit when utility power dips below 80-85% of nominal voltage.

- Preceptor Remote Series (6V Units):

    - The unit shall be constructed of aluminum.

    - The unit shall be furnished with a power canopy that houses the battery, input transformer and printed circuit board.

    - The unit cabinets shall have a brushed Aluminum face with black frame.

    - The light source shall have Long-life, high-performance, low- power consumption.

    - The red LEDs of technology shall be provide an even illumination in the normal and emergency modes.

    - Battery input shall be 120/277 Vac, 60Hz, 0.06/ 0.03 A Max

    - Battery output shall be 60 Vrc, 9W/12W/24W.

    - Units shall be available with the following sealed maintenance-free battaries:

- Lead Calcium

- Cadmium Free, Environmentally Friendly Nickel Metal Hydride

    - The canopy unit shall have AC transformer, the charger circuitry and the sealed battery used to power the exit sign and the remote load.

    - The unit shall provide 90 minutes of battery powered emergency illumination.

- Preceptor Series (AC only, AC/DC and self-powered):

    - The LED lamps shall have high intensity long-life in Red or Green.

    - AC exit signs shall be either 120V or 277V.

    - AC/DC exit signs shall be either 120VAC or 277VAC, and 6 to 24VDC.

    - Self-powered exit signs shall be 120/277V.

    - The unit shall have advanced diagnostic circuitry.

    - The unit charger shall be fully automatic, solid state, and short circuit protected.

    - The battery shall be provides 90 minutes in emergency illumination.

    - The batteries are completely sealed maintenance-free Nickel-Cadmium for superior performance and long life.

    - The charger shall have  fully automatic, solid state, and short circuit protected.

    - Units shall be available with the following sealed maintenance-free battaries:

- Nickel-Cadmium

    - The exit sign shall have concealed knockouts for programmable directional chevrons.

    - Self-Powered models shall be provide a minimum of 90 minutes f battery powered emergency illumination.

    - The circuitry shall have a LED pilot light and test switch. .

    - All models shall have a universal 2-wire input capable of receiving the utility AC voltage from 120 through 277 Vac, 50/60 Hz.

- Premier Series:

    - The unit shall have durable, injection-molded, thermoplastic housing.

    - The unit shall have Universal, field-selectable snap in/out chevrons.

    - The unit shall have two faceplates, backplate for wall mount and easy install canopy for end and ceiling mounting.

    - The dual voltage input shall be 120 / 277Vac.

    - The Unit shall be optional Advanced Diagnostic circuitry, flasher/buzzer, fire alarmactivated flasher.

    - The standard equipment shall operate with a dual-voltage input of 120/277Vac with less than 3.5 Watts of consumption.

    - The faceplate shall be constructed of a durable high impact thermoplastic and come standard with snap in/out chevrons.

    - The LEDs shall provide illumination in normal and emergency operation and shall be mounted inside the exit housing.

    - The light source shall be long-life LEDs installed in a PCB strip.

    - The equipment shall stay illuminated at least 90 minutes upon AC failure.

    - The exit sign shall be approved for use in damp locations.

- Premier Thermoplastic Combination Series:

    - The unit comes with the Emergi-Lite Premier easy to install canopy and field-selectable   snap-in/out chevrons for quick and easy installation.

    - The unit shall be indirect refractive technology provides bright, even illumination.

    - The unit shall be choice of MR16 Halogen Lamps, shielded by a clear polycarbonate cover.

    - The unit shall be optional MR16 LED lamps with life expectancy 50,000+ hours.

    - The shall have sealed, maintenance-free, Lead Calcium or Nickel Metal Hydride batteries.

    - The dual voltage shall be input 120/277 VAC.

    - The unit shall be optional advanced diagnostic circuitry, flasher/buzzer, fire alarm activated flasher.

    - The standard equipment shall operate with a dual voltage input of 120/277VAC.

    - The unit shall be equipped with a test switch and a green pilot light, located on the face plate above the EXIT legend.

- Prestige DX Series (AC, AC/DC and self-powered):

    - The light source shall be 100% illumination in normal and emergency operation.

    - The unit housing shall be made from rugged textured die cast aluminum with a brushed aluminum faceplate.

    - Long life LED’s eliminate twice-a-year relamping typical of an incandescent light source.

    - All models are universal 2-wire, 120 to 277 Vac, 50/60 Hz.

    - The batteries shall be sealed, maintenance-free Nickel-Cadmium for superior performance and long life.

    - The units shall have provides 90 minutes of emergency operation.

    - Units shall be available with the following sealed maintenance-free battaries:

- Nickel-Cadmium

    - Units shall be choice of Models available with a Red or Green LED Light Source include

- AC-Only, universal 120 to 277 Vac, 50/60 Hz.

- AC/DC, 120 to 277 Vac input, 6 to 24 Vdc.

- 2 AC circuit, 120 to 277 Vac.

- Self-Powered, 120 to 277 Vac input.

- AC-Only signs are now standard as AC/DC

    - The light source shall be long life, high intensity light emitting diodes (LED).

    - The battery shall provide 90 minutes of emergency illumination, when upon failure of AC power.

- Prestige Economizer™ Series (AC, AC/DC and self-powered):

    - The unit shall operate with universal two-wire AC input voltage from 120Vac to 277Vac at less than 3 Watts for single and double face legends.

    - The unit shall operate with universal two-wire DC input voltage from 6V to 24Vdc.

    - The housing assembly shall be fabricated of extruded aluminum with a textured finish and color.

    - The canopy shall be of die-cast aluminum and allow for ceiling, wall, or end mount installation.

    - The light source shall be long-life LEDs installed on a PCB strip.

    - The acrylic panel shall have a curved contour.

    - The legend shall have six-inch high with ¾-inch stroke red letters on a clear background, unless otherwise specified.

    - The unit shall be equipped with field installed stick-on translucent directional indicators, to be installed in the field as required by the code.

    - The exit sign in a self-powered configuration shall be equipped with sealed Nickel-Cadmium batteries and perform minimum 90 minutes of emergency illumination upon AC failure.

- Prestige Series (AC only and Self-powered units):

    - The unit shall have a modular design of die cast components allow for surface or recess mounting without changing the aesthetic design of the spec.

    - AC input for AC-only and Self-powered models shall be 120 to 277VAC, 50/60Hz, AC-only signs use 3 watts max, Self-powered signs use 3.5 watts max while recharging batteries.

    - The unit shall be available with the following sealed maintenance-free battery:

a.	Nickel-Cadmium

    - The unit shall have solid state relay automatically and instantly transfers lamp load upon failure of AC supply.

    - The unit shall close tolerance electronic circuit activates emergency unit when utility power dips below nominal voltage.

    - The charger shall be current limited and short circuit proof. Its regulation shall be +/-1%.

    - The unit shall have combination push button test switch and LED AC indicator light.

    - The self test will test the unit for 30 seconds every 30 days, 30 minutes every 60 days and 90 minutes annually.

- Prestige Floor Proximity Exit :

    - The units shall be either surface or recessed mount design made from die cast aluminum.

    - The stand alone AC-only and Self-powered units shall be 120/277Vac dual voltage.

    - LED’s provide excellent visual performance, high reliability and low maintenance costs. Red LEDs are of ALINGAP technology.

    - The unit’s batteries and circuitry shall be inside the housing.

    - Continuous self-diagnostic monitoring shall be standard.

    - Batteries shall be sealed, maintenance-free Nickel-Cadmium for superior performance and long life.

    - Universal knock-out chevrons shall be standard on exit door.

    - The unit shall provide 90 minutes of emergency operation and remote power for proximity exit sign.

    - The unit shall be available with the following sealed maintenance-free battery:

a.	Nickel-Cadmium

    - The self-test/diagnostic shall self test for 30 seconds every 30 days, 30 minutes every 60 days and 90 minutes annually.

- Prestige Series X40 LED Series (AC only and Self-powered units) :

    - The equipment shall operate with universal two-wire AC input voltage from

120Vac to 277Vac, AC-only signs use 2 watts max, Self-powered signs use 2.5 watts max while recharging batteries.

    - The trim assembly shall be fabricated of die cast aluminum and consist of a universal satin-coated steel back box. The back box shall be provided with conduit knockouts on top, back, and end. The trim plate shall attach to the housing assembly with two (2) torsion spring retainers thereby eliminating all visible screws or hardware.

    - The unit shall be available with the following sealed maintenance-free battery:

a.	Nickel-Cadmium

    - LED light strip shall be contained within the trim plate. Red LED technology shall be ALINGAP.

    - The polished acrylic face panel shall have precision etched 6” high and 3/4” inch stroke red letters with a white clear or mirror background.

    - The equipment shall be provided with bar hangers to facilitate installation.

    - The exit sign in a self-powered configuration shall stay illuminated during emergency operation for at least 90 minutes upon AC failure.

    - The charger shall be current limited and short circuit proof. Its regulation shall be +/-1%.

    - The unit shall have combination push button test switch and LED AC indicator light.

    - The self test will test the unit for 30 seconds every 30 days, 30 minutes every 60 days and 90 minutes annually.

- Survive-All SVX Combo Series (6 and 12 Volts Units):

    - The combination unit shall be able to provide exit signage and the emergency lighting with its entire electronics and power source in a slim one-piece compact sealed NEMA 4X-rated housing.

    - The emergency lighting MR16 heads shall be located at the bottom of the unit and covered by a sealed clear lens made of UV-stabilized polycarbonate. These emergency lighting heads shall be equipped with an innovative swivel system allowing for up to a 180° rotation in order to provide for an illumination in any direction of the path of egress.

    - The unit shall be NEMA 4X-rated and designed specifically for high abuse areas, wet and damp locations, as well as for cold weather applications (CW4 option).

    - The exit signage faceplate(s) shall be constructed of heavy-duty vandal-resistant polycarbonate and features an even illuminated legend.

    - The legend light source shall be composed of high efficiency light emitting diodes (LED).

    - The Emergi-Lite Advanced Diagnostic Micro-controller board shall supply the rated load for a minimum of 90 minutes to 87.5% of the rated battery voltage.

    - The unit shall be rated 120/277Vac, 60Hz.

    - The unit shall be available with the following sealed maintenance-free battery:

a.	Nickel-Cadmium

    - The charger shall periodically pulse-charge the battery in stand-by mode. This pulse-plus charger promotes long battery life and reduces the potential for grid corrosions. Its charge voltage is factory set to +/-1% tolerance and temperature compensated.

    - The charger incorporates Lockout and Brownout Circuits, and Low Voltage Disconnection. It protects the unit from over-current, short-circuit, and reverse polarity.

    - This unit shall self-test for 1 minute every 30 days, 30 minutes on the 6th month and 90 minutes every 12 months.

    - The unit shall be supplied with a magnetic test switch.

    - A “Service-Required” lamp shall be located near the test switch and flash when a fault is detected.

    - A LED-based diagnostic display shall be located inside the equipment and shall identify the source of failure (battery, charger, circuitry, or lamps).

- Survive-All SVX Exit (AC only, AC/DC and Self-powered units):

    - The exit housing shall be molded polyvinyl chloride in either white or black. A universal mounting pattern shall be available on single face signs for back mounting to a wall or surface.

    - All models shall come equipped with a canopy for ceiling or end mount applications.

    - The faceplate and canopy shall have gasketing available for a secure, water-tight seal.

    - The light source shall be high intensity, long-life light emitting diodes (LED’s). LED’s shall provide even illumination, at the same intensity during AC operation and in the emergency mode.

    - LED’s shall be mounted within the exit housing but not along the face or wording.

    - An LED sensitive ink diffuser shall be mounted on the face to provide full 3/4” letter stroke with even illumination. Red LED technology shall be ALINGAP.

    - All models shall have a universale 2-wire input of 120 to 277VAC 50/60Hz.

    - AC/DC units shall have a DC output of 6 to 24VDC.

    - The unit shall be available with the following sealed maintenance-free battery:

a.	Nickel-Cadmium

    - In the emergency mode the battery shall provide a minimum of 90 minutes run time.

    - Self Testing/Self diagnostics shall be standard on all self powered signs.

    - The circuit shall have a single “service required” LED visible to the user.

    - A detailed diagnostic display will be found internally to the unit and isolate the fault to the battery charger board or LED lamps.

    - The self testing software will simulate a power failure and transfer the light source to the battery for 30 seconds every 30 days, 30 minutes every 60 days and 90 minutes annually.

    - The unit shall be supplied with an AC pilot light and a magnetic proximity test switch for manual testing.

    - The charger shall be fully automatic, solid state, temperature compensated and short circuit protected.

- X10 LED Series (AC only, AC/DC and Self-powered units):

    - The housing shall be constructed of 20 gauge steel, with a tough epoxy powder finish in black or white.

    - The stencil face shall have field programmable knock-out directional arrows.

    - The unit shall have Long-Life LEDs which insure a high-illumination, even distribution of the light on the legend.

    - The unit shall operate with universal two-wire AC input voltage from 120Vac to 277Vac, 50/60Hz.

    - The unit shall operate with universal two-wire AC/DC models voltage from 6 to 24Vdc.

    - The unit shall be available with the following sealed maintenance-free battery:

a.	Nickel-Cadmium

    - Battery output shall be 6 V fused circuit.

    - In the emergency mode the battery shall provide a minimum of 90 minutes run time.

    - The unit shall have solid state relay automatically and instantly transfers lamp load upon failure of AC supply.

    - The unit shall close tolerance electronic circuit activates emergency unit when utility power dips below nominal voltage.

    - The charger shall be current limited and short circuit proof. Its regulation shall be +/-1%.

    - The unit shall haven test switch and dual diagnostic LED indicator lights, hi-charge and AC pilot.

PART 3 – EXECUTION

3.01	INSTALLATION

- Installation shall be in accordance to the NEC, CEC and manufacturer’s instructions.

END OF SECTION